| Project Name : | Enter Project Name | Type Of Panel : | PLC Panel |
| --- | --- | --- | --- |
| Project No : | Enter PISPL Project Number | Drawing No: | Drawing Number |
| Client : | Enter Client Name | End User : | Enter End User |

| VISUAL INSPECTION |  |  |  |  |  |  |  |  |  |  | Reference : |  | As per Approved Drawing |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Panel Dimensions (mm) |  | Height |  | 199999 |  |  | Width | 199999 | Depth |  |  | 199999 |  |  |
| Panel IP |  | IP-42 |  |  |  |  | Panel Colour code |  | RAL7035 |  |  | Components Mounting |  | OK |
| Nameplate |  | OK |  |  |  |  | Lock & Gasket |  | OK |  |  | Component Labeling |  | OK |
| Electrical Earthing | OK |  |  |  |  | Electronics Earthing |  |  |  | OK |  | Wiring |  | OK |
| Terminal Marker | OK |  |  |  | Ferruling |  |  |  |  | OK |  | Crimping & Tightness |  | OK |

| RAW MATERIALS & BROUGHT OUT ITEMS |  |  |  |  |  |  |  |  |  |  | Reference : |  | As per approved BOM |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PLC Modules | OK |  | SMPS | OK | MCBS |  |  | OK | Relay & Lamps |  |  |  |  | OK |
| Other Items | OK |  | Cables Make |  |  | KEI |  | Earthing Cables |  |  |  |  |  | 1 Sqmm Green |
| DI/DO Signal Cables |  | 0.5 Sqmm Shielded Cable |  |  |  |  |  | AI/AO Signal Cables |  |  |  | 0.5 Sqmm Yellow & Blue |  |  |
| Power cable |  | 2.5,1.5 Sqmm RED, BLACK |  |  |  |  |  | Communication Cables |  |  |  | Ethernet RJ45 |  |  |
| Any Other Cables |  | 1.0 Sqmm Grey cable for Control Wiring |  |  |  |  |  |  |  |  |  |  |  |  |

| TESTING PROCESS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Continuity Test | Tested as per drawing & Found OK |  | Power Test |  | Tested with 230VAC non ups supply |  |  |
| Software Test | Hardware configuaration done through Simatic Manager V 5.6 with CPU 315-2PN/DP |  |  |  |  |  |  |
| DI/DO Test | From Software forcing and sorting done for DI,DO |  |  | AI/AO Test |  |  | Tested from Software |
| Communication Check | PLC to RIO communication tested and found OK |  |  | Logic Test |  |  | Tested with Demo logic |
| Other Functionality Check | Multimeter, Continuity Tester |  | Hardware used for Testing |  |  | Simatic Manager |  |
| Software used for Testing | Simatic Manager |  | Calibration |  |  | Not applicable |  |

COMMENTS OF TESTING ENGINEER

COMMENTS OF PROJECT MANAGER

COMMENTS OF PURCHASE

| FINAL ACCEPTANCE | Accepted | DISPATCH CLEARENCE | Need end user confirmation |
| --- | --- | --- | --- |